## Slide 1
Wet Chemical Kitchen Suppression System Inspections
FSCI Presents:

## Slide 2
SYSTEM INFORMATION | 
The system being reviewed is designed per: | IBC – 2015
 | IFC – 2015
 | IMC – 2015
 | NFPA 17A – 2013
 | NFPA 10 – 2013
Number of protected hoods: | Two
System manufacturer: | Ansul
Number of systems: | One
Number of agent tanks per system: | Two
Size of agent tanks: | 3 gallons / 3 gallons
Allowable number of flow points per tank: | 11 / 11
Number of flow points used per tank: | 9 / 11
Allowable number of flow points per system: | 22
Total number of flow points used per system: | 20
Manual pull station provided: | Yes
Gas valve provided: | Yes
Adequate placement of detectors: | Yes
Verify plan review letter specifics
  Codes used
  Number of Hoods
  Manufacturer
  Size and Number of Tanks
  Total Flow points allowed and used

## Slide 3
HOOD #1 INFORMATION | 
Hood size: | 9' - 0" x 2' - 9"
Plenum nozzle type: | 1N
Plenum nozzle maximum coverage area: | 10' - 0"
Exhaust duct size: | 10" x 17"
Exhaust duct perimeter: | 54"
Exhaust duct nozzle type: | 2W
Exhaust duct nozzle maximum perimeter: | 100"
APPLIANCE INFORMATION | 
Type of appliance: | Griddle
Overall appliance size: | Not specified
Hazard area: | 36" x 24"
Nozzle type shown on plans: | 260
Nozzle location related to hazard area: | 0" - 2" inside hazard area perimeter
Nozzle aim point: | Center of hazard area
Nozzle height above hazard: | 30" to 50"
Nozzle maximum coverage area: | 48" x 30"
Shown or provided with a back shelf: | No
Verify plan review letter specifics
  Hood sizes
  Nozzle manufacturer, type and numbers
  Appliance to be protected
  Nozzle locations

## Slide 4
Appliances must match the design drawings:
  Completely under the hood
  Appliances in correct location

## Slide 5
Appliances locations must match the design drawings:
  Appliance on solid legs
  Appliances on wheels must be secured in place
Notes: Movable appliances must have cable restraints, channel or guide to insure appliances go back to the correct position after cleaning and maintenance.

## Slide 6
Separation of fryers and surface flame appliances:
  All deep fat fryers must be separated from surface flame by 16” space
  If a steel or tempered glass baffle is used instead of separation, minimum 8” height between adjacent appliance.
  If the fryer and surface flames appliance are on different horizontal planes a minimum of 8” is measured from the higher of the two
Notes: The baffle is removable, after the acceptance test the baffle will be lost or removed. Its best separate those appliances
with a table or griddle

## Slide 7
Verify nozzles:
  Verify nozzles installed match those on the plans and letter
Notes: Marking on the nozzles are very difficult to see

## Slide 8
Verify nozzles:
  Verify nozzle locations, heights and aim points match those on the plan review letter
Notes: Heights are dictated by the type of nozzle and appliance, aim point is normally center of hazard being protected

## Slide 9
Tanks and manifolds
  Check tanks size to plan review letter
  Manifold actuation lines required for simultaneous activation

## Slide 10
System Piping
  All pipe installed must be stainless or steel
  Galvanized pipe is not allowed

## Slide 11
Fusible links are installed at proper locations:
  Above each appliance
  At top of hood to vertical ducts

## Slide 12
Fusible Links Installed:
  Above Each Cooking Appliance
Exception:
Not if appliances are located directly below exhaust
  At Each Exhaust Duct
  Proper Temperature Rating Based on Appliance

## Slide 13
Gas and electric must shut down upon activation :
  All sources of fuel and power to equipment under the hood must shut down.
Notes: Solid fuel cooking operations shall not be required to shut down.

## Slide 14
Manual System Activation must be:
  Clearly Labeled
  Mounted 42”- 48” Off Floor
  Located 10’ to 20’ Away in Direction of Exit
  Activate with a maximum 40 pounds of force
  Maximum 14 inches of Movement

## Slide 15: Prefer balloons: for each nozzle, to verify pipes are connected and/or nozzle blocked grease

## Slide 16
When the system is activated:
  Exhaust Fans Should Continue to Operate upon System Activation
  Make-up Air Located Outside the Hood does not need to Shut Down
  Balloons Should Fill Equally
  Alarm Should Activate
  Gas / Electric Shut Down

## Slide 17
If system is connected to the building fire alarm system:
  Verify Notification Devices Activate
  Verify Panel Zoned for Kitchen Hood
  May Only be a Local Alarm

## Slide 18
Approved signs are required to be installed
  Often Missed by the Installer

## Slide 19
Portable extinguisher requirements:
  K-Class Wet Chemical
  30’ from Protected Hood
  Filled with Proper Agent
  Mounted in Area not Prone to being Blocked or Hidden
  Current Tag

## Slide 20
Mechanical system related items:
  Although this is the wet chemical inspection, check it anyway.
  Fan Interlocks
  (Automatic Fan Operation)
  Cable Restraints
  Roller Guides

## Slide 21
Completing the Inspection
  Have Technician Place System in Service
  Advise Technician to Place Alarm In Service

## Slide 22
Completing the Inspection
  Collect As-Built

## Slide 23
Completing the Inspection
  Explain Any Issues or Problems
  Complete Report